# FAQs

# How do I perform ATV630 and ATV930 Basic Programming?

# Issue:
Basic Programming on an Altivar Process Drive.

Product Line:
Altivar Process Drive (ATV630, ATV930, ATV650, ATV950, ATV660, ATV960, ATV680, ATV980)

Environment:
All serial numbers for Altivar Process Drive 

Cause:
Initial setup / maintenance

Resolution:
Using the keypad or our SoMove programming software, be sure to go through the Simply Start Menu to perform your basic settings:

From the Main Menu select [Simply start]:

[Motor Standard] bFr – 50Hz IEC or 60Hz NEMA- motor nameplate
[Nominal motor power] nPr – Motor HP - motor nameplate
[Nom Motor Voltage] UnS – Motor voltage - motor nameplate
[Nom Motor Current] nCr – Motor FLA - motor nameplate
[Nominal Motor Freq] FrS – 60Hz in the US - motor nameplate
[Nominal Motor Speed] nSP – Actual motor max speed, not Synchronous speed unless it is a synchronous motor - motor nameplate
[2/3-Wire Control] tCC – Factory default is '2-Wire Control' 
[Max Frequency] tFr – Max frequency of the motor, usually 60Hz - motor nameplate
[Autotuning] tUn – No Action, Apply Autotuning, Erase Autotuning 
[Autotuning Status] tUS – Displays 'Not Done' unless Autotuning is performed
[Motor Th Current] ItH – Motor thermal current - motor nameplate - used to set the motor overload protection level
[Acceleration] ACC – Acceleration time in seconds

# [Deceleration] dEC – Deceleration time in seconds
[Low Speed] LSP – Minimum speed, drive will never run lower than this speed when given a run command
[High Speed] HSP – Maximum speed, drive will never run higher than this speed when given a run command


In many instances these parameters will be enough to sufficiently program a drive. If any further programming is required (such as PID, command/reference switching, hoisting, etc), please refer to the applicable Programming Manual for your drive.

Refer to the applicable manual for further details:
ATV600 series Programming Manual 
ATV900 series Programming Manual

# _________________________________________________________________________________

# How to save the parameters in the keypad and upload to another identical ATV630 drive.

Issue:
Trying to save the parameters in the keypad and upload them to another identical ATV630 drive.

Product Line:
 ATV630 drives

Environment:
Keypad

Cause:
Transferring files

Resolution:
Go to Main menu and scroll down to menu 7: File Management and press Ok.
Select 7.1-Transfer config file- select copy from the drive ( to save to the keypad) or select Copy to the drive (to upload the keypad setting to the drive)

# _________________________________________________________________________________

# Does the ATV600 series drive have a multi-motor function?

Issue:
ATV600 series drive have a multi-motor function.

Product Line:
Altivar Process, ATV630, ATV650, ATV660, ATV680

Resolution:
ATV6xx does not have a multi-motor management function.  The multi-motor feature is available in the ATV9xx series drive .

# _________________________________________________________________________________

# Can we use PID function and Preset Speeds with the Altivar Process Drives?

Issue:
Can the Altivar Process Drive be programmed to use Preset Speed when also using PID Control?

Product line:
Altivar Process, ATV630, ATV930

Environment:
all

Cause:
Preset does not have priority over the PID function on Channel 1.  

Resolution:
The PID loop won't acknowledge a preset speed on the same channel.  Use a Digital input programmed for PID Auto/Manual to take it out of PID.  Then you can turn on a preset speed. 
You can set the same Digital Input to both functions if his Access Level is set to Expert.